## Slide 1
ELECTRICAL SAFETY · INTERNSHIP PROJECT
Earth Fault Loop Impedance
(Zs) Chatbot
An electrical-safety web assistant that computes Zs from earthing measurements and verifies disconnection compliance.
Bharat Reddy
Roll 24WU0104089T · B.Tech AIML
Woxsen University, School of Technology
PROTECTIVE EARTH

## Slide 2
THE PROBLEM
Why earth fault loop impedance matters
When a live wire faults to earthed metalwork, the fault current must be large enough to trip the breaker fast.
That current depends on the loop impedance Zs. If Zs is too high, the current is too small, the breaker is slow to trip, and the metalwork stays dangerously live.
This project turns that safety check into a simple chatbot anyone can use.
High Zs = Danger
High loop impedance
→ small fault current
Small fault current
→ breaker trips slowly
Slow disconnection
→ metal stays live
Live metalwork
→ risk of electric shock

## Slide 3
THE ENGINEERING
The formulas behind the calculation
Loop impedance
Zs = Ze + (R1 + R2)
Ze = earthing system, R1 = phase conductor, R2 = earth conductor
Earthing system
1/Ze = Σ 1/R_pit + 1/R_grid
All earth pits and the grid combine in parallel to give Ze
Compliance limit
Zs ≤ (2/3) × (U0 / Ia)
U0 = 230 V, Ia = trip current = type × rating (B×5, C×10, D×20)
Standards
pit < 5 Ω grid < 1 Ω
Recommended resistance for each electrode and the overall grid

## Slide 4
WHAT I BUILT
An electrical-safety chatbot web app
Natural-language input
Type measurements in plain words: "3 pits 4.2, 5.1, 3.8 Ω, grid 0.9 Ω, Type C 32A"
Automatic Zs calculation
Combines electrodes in parallel, computes Zs, and checks the disconnection limit
Instant PASS / FAIL verdict
Clear compliance result with the margin and an engineering recommendation
Electrical-only assistant
Answers electrical questions; politely declines anything off-topic
Zs Agent
3 pits 4.2, 5.1, 3.8 Ω, grid 0.9 Ω, Type C 32A
Zs = 0.553 Ω (4 electrodes)
Limit (Type C 32A) = 0.479 Ω
FAIL — exceeds by 15%
"what is the weather?"
I only answer electrical questions.

## Slide 5
HOW IT WORKS
Four steps on every message
1. Understand
Parse the message and pull out pit, grid, R1, R2, breaker type and rating
2. Calculate
Combine electrodes in parallel → Ze, then Zs, then the allowed limit
3. Assess
Compare Zs to the limit → PASS or FAIL, with margin and advice
4. Reply
Send the result back to the chat; flag any electrode over its guideline
The web page (frontend) only displays the conversation — all the physics runs in the Python backend.

## Slide 6
STAYS ON-TOPIC
An electrical-only chatbot
Answers
"What is an MCB and how do the types differ?"
"Why do we need earthing?"
"How can I reduce earth resistance?"
"3 pits 4.2, 5.1, 3.8 Ω, grid 0.9 Ω, Type C 32A"
Declines
"What is the weather today?"
"Who won the cricket match?"
"Write me a poem."
"I'm an electrical-engineering assistant, so I can only answer questions about electrical subjects."

## Slide 7
WORKED EXAMPLE
Three pits + grid on a Type C 32 A breaker
INPUT pits 4.2, 5.1, 3.8 Ω · grid 0.9 Ω · Type C, 32 A · U0 = 230 V
Ze
0.553 Ω
parallel of pits + grid
Zs
0.553 Ω
Ze + (R1 + R2)
Max Zs
0.479 Ω
⅔ × (230 / 320)
Verdict
FAIL
exceeds limit by 15%
The earthing is good, but for a Type C 32 A breaker the loop impedance is slightly too high — the fix is a lower Ze (more electrodes / soil treatment) or a more sensitive breaker.

## Slide 8
TECHNOLOGY
How it is built
Backend — Python + Flask
Calculation engine, natural-language parser, electrical topic-guard and Q&A, exposed through a small REST API (/chat).
Frontend — HTML, CSS, JavaScript
A clean chat interface that sends each message to the backend and displays the reply, with a PASS / FAIL colour cue.
Logic — Regex parsing + engineering rules
Deterministic: numbers are computed in code, never guessed, so results are exact and repeatable.
Runs locally on localhost
Single command — python3 app.py — serves the whole app in the browser; no internet needed.

## Slide 9
OUTCOME & NEXT STEPS
What works today, and what's next
Achieved
Working full-stack chatbot web app
Accurate Zs calculation and PASS / FAIL compliance check
Plain-language input, no forms to fill
Electrical-only behaviour with a built-in Q&A
Next steps
Cover more electrical topics (transformers, cable sizing, RCD ratings)
Export a session as a PDF report for documentation
Split into a React frontend + Flask backend
Validate against the full governing standard and site data